**PHE 3C22 CAT 3 Lab Resolution Summary**

|  |  |  |
| --- | --- | --- |
| Previous status | Current Status | Comments |
| Ventilation Verification | On target to complete having tested Class 1 and Class 3 MSCs.AHU Static profile taken as baseline commissioning value.TodayHEPA Integrity TestsRoom Integrity (Sealabilty)Pressure Decay Tests are planned for later today | In progress |
| BMS Controls | Annual PPM completeHVAC Controls Fail Safe complete | Door interlock repairs still in progress so this element of the PPM was not carried out.All HVAC Failsafe Tests Passed |
| Door Interlocks | Remedial work in progress regarding interface between previously installed delay relays and Prowatch system, currently working to provide best solution | New interlock circuit board installedIn progress |